Network
IN BOARD OOMEN02
BACnet Display
Alice and George
Boost
Sushi Sushi
The Kitchen #1
The Kitchen #2
ECB350-1
ECB350-2
ECB350-3
ECB350-4
ECB350-5
Epicure
ECB350-6
Legend
STANDALONE FAN CONTROL ONLY
TCP/IP CAT5
KNX-EIB
MODbus RS485
BACnet RS485
SubLAN RS485
AMENDMENT
REV
DATE
PROJECT TITLE:
MJS
DRAWN:
CHECK:
A
PRELIMINARY
SCUH Retail Tenancies
B
7-10-16
PQ-1006
JOB No:
REVISION:
ADD DDC TERMINALS
18-1-17
SSNE-01
Controlworks Qld Pty Ltd
DRAWING No:
CLIENT:
Shop Steel
www.controlworks.com.au
Network Install Layout
DRAWING NAME:

---
FCU-OOMEN018
Common power supply
For all controls by others
CB
P
CB Board
24 VAC TX1 240VAC
24 VAC
N
Space Temp
GND
SA Temp
Fan Status
Dirty Filter
SAF Request 0-10V to EC Fan
Chilled Water Valve
C
R2 Run Signal to DDC
OA Damper
D
RS485
Incomming
outgoing
CAT5 PATCH LEAD
DDC INTERFACE TERMINALS IN CONTROL PANEL
FCU: OOMEN018
Alice and George
BACnet
Mac Add: 4
Device Instance: 364004
R2
TO DDC - FCU RUN STATUS
PULSE
METER
TO DDC – PULSE METER
SSCE-01
FCU Conection Diagram
°C
ECF
R
UI10
UI8
UI9
UI6
UI7

---
FCU-OOMEN019
R1 SAF Request
FCU: OOMEN019
Boost Juice
Mac Add: 5
Device Instance: 364005
SSCE-02

---
FCU-OOMEN020
R1 SAF Request
FCU: OOMEN020
KEF: H-01
Sushi Sushi
Mac Add: 6
Device Instance: 364006
SSCE-03

---
FCU-OOMEN021
R1 SAF Request
H-02 KEF PB
R3 H-02 KEF Request
R4 H-02 KEF Run LED
R5 H-02 KEF Fault LED
OA Damper Make Up Air
FCU: OOMEN021
KEF: H-02
The Kitchen
Mac Add: 7
Device Instance: 364007
R3
TO DDC – EF RUN REQUEST
SSCE-04

---
FCU-OOMEN023
R1 SAF Request
H-03 KEF Fan Status
H-03 KEF Dirty Filter
DW KEF Status
OA Damper 2
FCU: OOMEN023
KEF: H-03
The Kitchen
Mac Add: 8
Device Instance: 364008
SSCE-05
Gas Interlock

---
H-04 & H-05
H-04 KEF PB
H-04 KEF Fan Status
H-04 KEF Dirty Filter
H-05 KEF PB
R1 H-04 KEF Request
H-05 KEF Fan Status
R2 H-04 KEF Run LED
H-05 KEF Dirty Filter
R3 H-04 KEF Fault LED
R4 H-05 KEF Request
R5 H-05 KEF Run LED
R6 H-05 KEF Fault LED
KEF: H-04 and H-05
Epicure
Mac Add: 9
Device Instance: 364009
R4
TO DDC – EF RUN REQUEST
SSCE-06
KEF Conection Diagram
R7 Gas Interlock

---
FlowMeter
Fit theWZU-P2 Pulse Module to the module one location as shown
Pulse output to connect direct to BMS system
SSCE-07
Typical Flow Meter

---
Wall Plates
KEF Control
P.B.
START
GREEN
Increase
RUN
RED
Enter/Select
FAULT
Decrease
EC
Smart
Vue
KEF Control Station
FCU Control Station
SSCE-08
Control Stations

---
Background
MARK UP
23-1-17